## Sheet 1
Nomenclature LIKE :Nomenclature, Building = 'KING PV'
Status:IN SERVICE
CMMS ID | Equipment | Floor | Room | Serves | Nomenclature | Mfr | Model number | Serial No | Keyword | Warranty Date | Acquisition Date | Work Number | Work Description | Maintenance Type | Total Costs/WO | Task List
1 | E045886 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEATING WATER SYSTEM | N/A | N/A | N/A | SYSTEM |  | 2009-07-14
20" | E023931 |  |  |  | BUFFER, | VIPER | 2015 | VN-2015-06776 | SHOP EQ. |  | 2010-02-15 | WA10707 | MAINTENACE & REPAIR OF BUFFER, 20" | EQ-MAINT
| E024126 |  |  |  | AUTOSCRUB, STANDUP RIDER | WINDSOR | ISCRUB 20 | 10061370000142 | SHOP EQ. |  | 2011-01-01 | WA10773 | MAINTENACE & REPAIR OF AUTOSCRUB, STANDUP RIDER 20" | EQ-MAINT | 253.18
ASU2 | E037171 | G | 0749 | HXU2 HEATING WATER | AIR SEPARATOR UNIT | TACO | 49025AT | N/A | SEPARATOR | 2010-07-14 | 2009-07-14 | W831827 | AIR SEPARATOR UNIT, KING PV, 1 | PM |  | 1. BLOW DOWN UNIT TO REMOVE ANY DEBRIS FROM THE SYSTEM.
ASU2 | E037171 | G | 0749 | HXU2 HEATING WATER | AIR SEPARATOR UNIT | TACO | 49025AT | N/A | SEPARATOR | 2010-07-14 | 2009-07-14 | W885256 | AIR SEPARATOR UNIT, KING PV, 1 | PM |  | 1. BLOW DOWN UNIT TO REMOVE ANY DEBRIS FROM THE SYSTEM.
ASU2 | E037171 | G | 0749 | HXU2 HEATING WATER | AIR SEPARATOR UNIT | TACO | 49025AT | N/A | SEPARATOR | 2010-07-14 | 2009-07-14 | W939903 | AIR SEPARATOR UNIT, KING PV, 1 | PM |  | 1. BLOW DOWN UNIT TO REMOVE ANY DEBRIS FROM THE SYSTEM.
ASU2 | E037171 | G | 0749 | HXU2 HEATING WATER | AIR SEPARATOR UNIT | TACO | 49025AT | N/A | SEPARATOR | 2010-07-14 | 2009-07-14 | WA06954 | AIR SEPARATOR UNIT, KING PV, 1 | PM | 11 | 1. BLOW DOWN UNIT TO REMOVE ANY DEBRIS FROM THE SYSTEM.
ASU2 | E037171 | G | 0749 | HXU2 HEATING WATER | AIR SEPARATOR UNIT | TACO | 49025AT | N/A | SEPARATOR | 2010-07-14 | 2009-07-14 | WB06689 | AIR SEPARATOR UNIT, KING PV, 1 | PM |  | 1. BLOW DOWN UNIT TO REMOVE ANY DEBRIS FROM THE SYSTEM.
ASU2 | E037171 | G | 0749 | HXU2 HEATING WATER | AIR SEPARATOR UNIT | TACO | 49025AT | N/A | SEPARATOR | 2010-07-14 | 2009-07-14 | WC07008 | AIR SEPARATOR UNIT, KING PV, 1 | PM | 29.5 | 1. BLOW DOWN UNIT TO REMOVE ANY DEBRIS FROM THE SYSTEM.
BATTERY | E023927 |  |  |  | VACUUM, SWEEPER 24" - | EAGLE POW | TK464E | 800131939 | SHOP EQ. |  | 2010-02-15 | WA11237 | MAINTENACE & REPAIR OF VACUUM, SWEEPER 24" - BATTERY | EQ-MAINT
BEF1 | E037169 | G | 0749 | ERV-1 | BUILDING EXHAUST FAN | COMEFRI | P3604002A | 2009/5 | FANS | 2010-07-14 | 2009-07-14
BPD1 | E036960 | G | 0749 | MAKE-UP FOR HXU2 | BACKFLOW PREVENTION DEVICE | APOLLO | RP40204T2 | 175498 | BACKFLOW | 2010-07-14 | 2009-07-14 | W843057 | BACKFLOW PREVENTION DEVICE, FAC3MECH, 1 | PM |  | 1. Perform appropriate backflow preventer test as described in the EPA Cross Connection Control Manual. Complete the "Backflow Prevention Device Test and Maintenance Report"
BPD1 | E036960 | G | 0749 | MAKE-UP FOR HXU2 | BACKFLOW PREVENTION DEVICE | APOLLO | RP40204T2 | 175498 | BACKFLOW | 2010-07-14 | 2009-07-14 | W896164 | BACKFLOW PREVENTION DEVICE, FAC3MECH, 1 | PM | 106 | 1. Perform appropriate backflow preventer test as described in the EPA Cross Connection Control Manual. Complete the "Backflow Prevention Device Test and Maintenance Report"
BPD1 | E036960 | G | 0749 | MAKE-UP FOR HXU2 | BACKFLOW PREVENTION DEVICE | APOLLO | RP40204T2 | 175498 | BACKFLOW | 2010-07-14 | 2009-07-14 | W950932 | BACKFLOW PREVENTION DEVICE, FAC3MECH, 1 | PM |  | 1. Perform appropriate backflow preventer test as described in the EPA Cross Connection Control Manual. Complete the "Backflow Prevention Device Test and Maintenance Report"
BPD1 | E036960 | G | 0749 | MAKE-UP FOR HXU2 | BACKFLOW PREVENTION DEVICE | APOLLO | RP40204T2 | 175498 | BACKFLOW | 2010-07-14 | 2009-07-14 | WA21518 | BACKFLOW PREVENTION DEVICE, FAC3MECH, 1 | PM |  | 1. Perform appropriate backflow preventer test as described in the EPA Cross Connection Control Manual. Complete the "Backflow Prevention Device Test and Maintenance Report"
BPD1 | E036960 | G | 0749 | MAKE-UP FOR HXU2 | BACKFLOW PREVENTION DEVICE | APOLLO | RP40204T2 | 175498 | BACKFLOW | 2010-07-14 | 2009-07-14 | WB20461 | BACKFLOW PREVENTION DEVICE, FAC3MECH, 1 | PM |  | 1. Perform appropriate backflow preventer test as described in the EPA Cross Connection Control Manual. Complete the "Backflow Prevention Device Test and Maintenance Report"
BPD1 | E036960 | G | 0749 | MAKE-UP FOR HXU2 | BACKFLOW PREVENTION DEVICE | APOLLO | RP40204T2 | 175498 | BACKFLOW | 2010-07-14 | 2009-07-14 | WB26682 | BACKFLOW PREVENTION DEVICE, FAC3MECH, 1 | PM | 57 | 1. Perform appropriate backflow preventer test as described in the EPA Cross Connection Control Manual. Complete the "Backflow Prevention Device Test and Maintenance Report"
BPD1 | E036960 | G | 0749 | MAKE-UP FOR HXU2 | BACKFLOW PREVENTION DEVICE | APOLLO | RP40204T2 | 175498 | BACKFLOW | 2010-07-14 | 2009-07-14 | WC18112 | BACKFLOW PREVENTION DEVICE, FAC3MECH, 1 | PM |  | 1. Perform appropriate backflow preventer test as described in the EPA Cross Connection Control Manual. Complete the "Backflow Prevention Device Test and Maintenance Report"
CDP1 | E037177 | G | 0749 | RTK4 | CONDENSATE PUMP | BELL & GOS | UG616 |  | PUMPS | 2010-07-14 | 2009-07-14 | WB19299 | CDP1-2 NOT RUNNING | PLUMBING | 114
CDP2 | E037178 | G | 0749 | RTK4 | CONDENSATE PUMP | BELL & GOS | UG616 |  | PUMPS | 2010-07-14 | 2009-07-14
CTK1 | E037175 | G | 0749 | HXU2 HEATING WATER | CHEMICAL TANK | J.L. WINGE | 5HD | 200 PSI AT 200 | TANKS | 2010-07-14 | 2009-07-14
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W827556 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W831776 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W831777 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W831778 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W836894 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 10.2 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W841137 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 10.2 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W842837 | CHILLED WATER COIL LAYUP - AIR DRY | PM | 76.5 | 1. WHEN YOU JUDGE THE TIME TO BE APPROPRIATE, ISOLATE THE COIL, PUMP ITS' CONTENTS BACK INTO THE SYSTEM AND PERFORM NORMAL AIR DRYING PROCEDURES. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO COIL LAYUP. IF THERE IS AN AUTOMATIC VALVE B
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W842840 | CLEAN CHILLED WATER STRAINER, ARMORY, 1 | PM |  | 1. FOLLOWING AIR HANDLER CHILLED WATER COIL LAY-UP IN THE FALL, REMOVE AND INSPECT STRAINER SCREEN. IF THERE IS A STRAINER IN THE MAIN BUILDING CHILLED WATER SUPPLY LINE, REMOVE AND INSPECT THIS SCREEN ALSO. IF THE SCREEN IS DIRTY, CLEAN IT AND REPLACE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W845082 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 15.3 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W845083 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W845084 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W845668 | ENERGY RECOVERY VENTILATOR, KING PV, 2 | PM | 81.6 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W849025 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 10.2 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W853066 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 20.4 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W853186 | CHILLED WATER COIL - RETURN TO SERVICE | PM | 51 | 1. WHEN WEATHER PERMITS, REFILL THE CHILLED WATER COIL AND RETURN THE EQUIPMENT TO COOLING SEASON OPERATION. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO FILLING THE COIL. 2. VERIFY THAT BYPASS VALVE BETWEEN RETURN AND SUPPLY LINES IS
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W854071 | AHU 1 - REPLACE KEYPAD ON VFD (WARRANTY) - CONFIRM: MARIO FILIPP | CONTROLS | 55
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W857363 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 15.3 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W862543 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 15.3 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W866695 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 53.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W870517 | ENERGY RECOVERY VENTILATOR, KING PV, 1 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W875530 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 10.7 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W879037 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 10.7 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W885177 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W887369 | ENERGY RECOVERY UNIT CYCLING ON/OFF - CONFIRM: MARK REDDISH | CONTROLS
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W888691 | CHILLED WATER COIL LAYUP - AIR DRY | PM |  | 1. WHEN YOU JUDGE THE TIME TO BE APPROPRIATE, ISOLATE THE COIL, PUMP ITS' CONTENTS BACK INTO THE SYSTEM AND PERFORM NORMAL AIR DRYING PROCEDURES. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO COIL LAYUP. IF THERE IS AN AUTOMATIC VALVE B
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W889620 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W893946 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W894918 | CLEAN CHILLED WATER STRAINER, KING PV, 1 | PM |  | 1. FOLLOWING AIR HANDLER CHILLED WATER COIL LAY-UP IN THE FALL, REMOVE AND INSPECT STRAINER SCREEN. IF THERE IS A STRAINER IN THE MAIN BUILDING CHILLED WATER SUPPLY LINE, REMOVE AND INSPECT THIS SCREEN ALSO. IF THE SCREEN IS DIRTY, CLEAN IT AND REPLACE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W898200 | ENERGY RECOVERY VENTILATOR, KING PV, 2 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W902324 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 16.05 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W906606 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W906740 | CHILLED WATER COIL - RETURN TO SERVICE | PM | 53.5 | 1. WHEN WEATHER PERMITS, REFILL THE CHILLED WATER COIL AND RETURN THE EQUIPMENT TO COOLING SEASON OPERATION. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO FILLING THE COIL. 2. VERIFY THAT BYPASS VALVE BETWEEN RETURN AND SUPPLY LINES IS
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W911973 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W916805 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W921170 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 10.7 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W925834 | ENERGY RECOVERY VENTILATOR, KING PV, 1 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W929891 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W934200 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W939830 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 49.05 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W943330 | CHILLED WATER COIL LAYUP - AIR DRY | PM | 109 | 1. WHEN YOU JUDGE THE TIME TO BE APPROPRIATE, ISOLATE THE COIL, PUMP ITS' CONTENTS BACK INTO THE SYSTEM AND PERFORM NORMAL AIR DRYING PROCEDURES. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO COIL LAYUP. IF THERE IS AN AUTOMATIC VALVE B
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W944354 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W948892 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W949778 | CLEAN CHILLED WATER STRAINER, KING PV, 1 | PM |  | 1. FOLLOWING AIR HANDLER CHILLED WATER COIL LAY-UP IN THE FALL, REMOVE AND INSPECT STRAINER SCREEN. IF THERE IS A STRAINER IN THE MAIN BUILDING CHILLED WATER SUPPLY LINE, REMOVE AND INSPECT THIS SCREEN ALSO. IF THE SCREEN IS DIRTY, CLEAN IT AND REPLACE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W953159 | ENERGY RECOVERY VENTILATOR, KING PV, 2 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W957707 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W962404 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W963702 | CHILLED WATER COIL - RETURN TO SERVICE | PM | 54.5 | 1. WHEN WEATHER PERMITS, REFILL THE CHILLED WATER COIL AND RETURN THE EQUIPMENT TO COOLING SEASON OPERATION. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO FILLING THE COIL. 2. VERIFY THAT BYPASS VALVE BETWEEN RETURN AND SUPPLY LINES IS
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W968031 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 16.35 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W972844 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 16.35 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W977394 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 10.9 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W978450 | ENERGY RECOVERY VENTILATOR, KING PV, 1 | PM | 427.3 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | W981524 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 55 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA03275 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 11 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA06874 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 82.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA12774 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 82.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA14941 | CHILLED WATER COIL LAYUP - AIR DRY | PM | 110 | 1. WHEN YOU JUDGE THE TIME TO BE APPROPRIATE, ISOLATE THE COIL, PUMP ITS' CONTENTS BACK INTO THE SYSTEM AND PERFORM NORMAL AIR DRYING PROCEDURES. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO COIL LAYUP. IF THERE IS AN AUTOMATIC VALVE B
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA16705 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 11 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA20189 | ENERGY RECOVERY VENTILATOR, KING PV, 2 | PM | 88 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA20227 | CLEAN CHILLED WATER STRAINER, KING PV, 1 | PM | 22 | 1. FOLLOWING AIR HANDLER CHILLED WATER COIL LAY-UP IN THE FALL, REMOVE AND INSPECT STRAINER SCREEN. IF THERE IS A STRAINER IN THE MAIN BUILDING CHILLED WATER SUPPLY LINE, REMOVE AND INSPECT THIS SCREEN ALSO. IF THE SCREEN IS DIRTY, CLEAN IT AND REPLACE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA24315 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 27.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA27983 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 22 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA29755 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | CONTROLS | 228.75
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA32327 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 16.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA32421 | CHILLED WATER COIL - RETURN TO SERVICE | PM | 82.5 | 1. WHEN WEATHER PERMITS, REFILL THE CHILLED WATER COIL AND RETURN THE EQUIPMENT TO COOLING SEASON OPERATION. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO FILLING THE COIL. 2. VERIFY THAT BYPASS VALVE BETWEEN RETURN AND SUPPLY LINES IS
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA37267 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 11 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA41413 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA43948 | ERV-1, EXHAUST STATIC ALARM | HVAC | 167.07
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA45152 | ENERGY RECOVERY VENTILATOR, KING PV, 1 | PM | 11 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WA48374 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 11 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB02824 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB06616 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB11639 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 233.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB14662 | CHILLED WATER COIL LAYUP - AIR DRY | PM | 162.4 | 1. WHEN YOU JUDGE THE TIME TO BE APPROPRIATE, ISOLATE THE COIL, PUMP ITS' CONTENTS BACK INTO THE SYSTEM AND PERFORM NORMAL AIR DRYING PROCEDURES. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO COIL LAYUP. IF THERE IS AN AUTOMATIC VALVE B
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB15512 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB19751 | CLEAN CHILLED WATER STRAINER, KING PV, 1 | PM |  | 1. FOLLOWING AIR HANDLER CHILLED WATER COIL LAY-UP IN THE FALL, REMOVE AND INSPECT STRAINER SCREEN. IF THERE IS A STRAINER IN THE MAIN BUILDING CHILLED WATER SUPPLY LINE, REMOVE AND INSPECT THIS SCREEN ALSO. IF THE SCREEN IS DIRTY, CLEAN IT AND REPLACE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB20036 | NIGHT CALL - ERV 1 LOW LIMIT - CONFIRM: MIKE HANSON | CONTROLS | 110.63
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB20246 | ENERGY RECOVERY VENTILATOR, KING PV, 2 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB22025 | LOW LIMIT ALARM, KING PAVILLION, ER-1 | CONTROLS | 177
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB23920 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 29 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB24337 | KING PAVILIAN ERU-1 OFF ON LOW LIMIT | HVAC | 147.5
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB27127 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 29 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB28049 | ERV1 WILL NOT STAY RUNNING | CONTROLS
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB31313 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 29 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB31394 | CHILLED WATER COIL - RETURN TO SERVICE | PM | 81.2 | 1. WHEN WEATHER PERMITS, REFILL THE CHILLED WATER COIL AND RETURN THE EQUIPMENT TO COOLING SEASON OPERATION. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO FILLING THE COIL. 2. VERIFY THAT BYPASS VALVE BETWEEN RETURN AND SUPPLY LINES IS
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB36337 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 58 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB40529 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 17.4 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB45335 | ENERGY RECOVERY VENTILATOR, KING PV, 1 | PM | 255.2 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WB48216 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 118.99 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC02715 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 29.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC06843 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 29.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC11933 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 561.93 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC15036 | CHILLED WATER COIL LAYUP - AIR DRY | PM | 141.6 | 1. WHEN YOU JUDGE THE TIME TO BE APPROPRIATE, ISOLATE THE COIL, PUMP ITS' CONTENTS BACK INTO THE SYSTEM AND PERFORM NORMAL AIR DRYING PROCEDURES. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO COIL LAYUP. IF THERE IS AN AUTOMATIC VALVE B
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC15840 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 17.7 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC20737 | ENERGY RECOVERY VENTILATOR, KING PV, 2 | PM | 118 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK AUTOMATIC DAMPERS AND ACTUATORS FOR CORRECT OPERATION. ACTUATE UNIT TO MAKE SURE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC20829 | CLEAN CHILLED WATER STRAINER, KING PV, 1 | PM | 70.8 | 1. FOLLOWING AIR HANDLER CHILLED WATER COIL LAY-UP IN THE FALL, REMOVE AND INSPECT STRAINER SCREEN. IF THERE IS A STRAINER IN THE MAIN BUILDING CHILLED WATER SUPPLY LINE, REMOVE AND INSPECT THIS SCREEN ALSO. IF THE SCREEN IS DIRTY, CLEAN IT AND REPLACE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC24289 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 29.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC28351 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM | 35.4 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC31451 | CHILLED WATER COIL - RETURN TO SERVICE | PM |  | 1. WHEN WEATHER PERMITS, REFILL THE CHILLED WATER COIL AND RETURN THE EQUIPMENT TO COOLING SEASON OPERATION. NOTIFY THE POWER PLANT AT 4-4926 AND YOUR SUPERVISOR PRIOR TO FILLING THE COIL. 2. VERIFY THAT BYPASS VALVE BETWEEN RETURN AND SUPPLY LINES IS
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC32537 | ENERGY RECOVERY VENTILATOR, KING PV, 4 | PM | 59 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
ERV1 | E037167 | G | 0749 | BUILDING | ENERGY RECOVERY VENTILATOR | VENMAR CES | W-2-071-PP-SC-CW-CW-P | SO005197-01 | ENERGY REC | 2010-07-14 | 2009-07-14 | WC36286 | ENERGY RECOVERY VENTILATOR, KING PV, 12 | PM |  | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. CHECK TO SEE THAT ENERGY WHEEL IS TURNING UNDER POWER, MOTOR IS RUNNING PROPERLY AND A
ETK2 | E037172 | G | 0749 | HXU2 HEATING WATER | EXPANSION TANK | TACO | CX-84-3 | X16825 | TANK/EXP | 2010-07-14 | 2009-07-14
EXL80 | E037156 | 1 | 1730 | OS ROOM 1734 | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
EXL81 | E037157 | 1 | 1750 | OS ROOM 1756 | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
EXL82 | E037158 | 1 | 1710 | HALLWAY INTO DESIGN CENTER | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
EXL83 | E037159 | 1 | 1720 | 1ST FLOOR NW EXIT | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
EXL84 | E037160 | G | 0710 | EXIT 0710-X2 | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
EXL85 | E037161 | G | 0710 | EXIT 0710-X1 | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
EXL86 | E037162 | G | 0730 | OS ROOM 0734 | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
EXL87 | E037163 | G | 0750 | OS ROOM 0756 | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
EXL88 | E046786 | G | 0720 | NEAR DOOR 0720-X1 | EXIT LIGHT | LIGHTALARM | SLEDARC | N/A | LIGHT | 2010-07-14 | 2009-07-14
FCU18 | E037179 | G | 0713 | ROOM 0713 | FAN COIL UNIT | STERLING | FSI-1045-10 | 04/22/09 | FAN COIL | 2010-07-14 | 2009-07-14
FCU19 | E037180 | G | 0710 | CORRIDOR 0710 | FAN COIL UNIT | STERLING | FSI-1045-10 | 04/22/09 | FAN COIL | 2010-07-14 | 2009-07-14
FCU20 | E037181 | G | 0720 | STAIRWELL 0720 | FAN COIL UNIT | STERLING | RWI-1130-04 | 04/22/09 | FAN COIL | 2010-07-14 | 2009-07-14
FCU21 | E037182 | 1 | 1760 | ENTRANCE 1760 | FAN COIL UNIT | STERLING | RWI-1130-10 | 04/22/09 | FAN COIL | 2010-07-14 | 2009-07-14
HANDLED | E024375 |  |  |  | VACUUM, | NOBLES | V-DMU-14 | 11D0004457 | SHOP EQ.
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | W850118 | HOOD EXHAUST FAN, KING PV, 2 | PM | 20.4 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM.. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY.
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | W876615 | HOOD EXHAUST FAN, KING PV, 1 | PM | 21.4 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY. 4. LUBR
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | W903535 | HOOD EXHAUST FAN, KING PV, 2 | PM | 21.4 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM.. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY.
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | W931181 | HOOD EXHAUST FAN, KING PV, 1 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY. 4. LUBR
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | W959092 | HOOD EXHAUST FAN, KING PV, 2 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM.. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY.
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | WA06924 | HOOD EXHAUST FAN, KING PV, 1 | PM | 22 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY. 4. LUBR
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | WA32366 | HOOD EXHAUST FAN, KING PV, 2 | PM | 22 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM.. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY.
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | WB06665 | HOOD EXHAUST FAN, KING PV, 1 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY. 4. LUBR
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | WB31350 | HOOD EXHAUST FAN, KING PV, 2 | PM | 40.6 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM.. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY.
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | WC07007 | HOOD EXHAUST FAN, KING PV, 1 | PM | 29.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY. 4. LUBR
HEF9 | E037164 |  |  | ROOM 0712, PAINT BOOTH | HOOD EXHAUST FAN | GREENHECK | WK-CD-WBND | 116618470902 | FANS | 2010-12-28 | 2009-12-28 | WC32603 | HOOD EXHAUST FAN, KING PV, 2 | PM | 47.2 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM.. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN. MAKE SURE THE FAN IS RUNNING SMOOTHLY.
HWP7 | E037173 | G | 0749 | HXU2 HEATING WATER | HOT WATER PUMP | TACO | 1911C1E1 | 4.6 DIA 02/09 | PUMPS | 2010-07-14 | 2009-07-14
HWP8 | E037174 | G | 0749 | HXU2 HEATING WATER | HOT WATER PUMP | TACO | 1911C1E1 | 4.6 DIA 02/09 | PUMPS | 2010-07-14 | 2009-07-14
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | W831826 | HEAT EXCHANGER UNIT, KING PV, 2 | PM |  | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | W857410 | HEAT EXCHANGER UNIT, KING PV, 2 | PM | 10.2 | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | W885255 | HEAT EXCHANGER UNIT, KING PV, 2 | PM |  | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | W912064 | HEAT EXCHANGER UNIT, KING PV, 2 | PM |  | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | W939901 | HEAT EXCHANGER UNIT, KING PV, 2 | PM | 21.8 | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | W968095 | HEAT EXCHANGER UNIT, KING PV, 2 | PM | 10.9 | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | WA06951 | HEAT EXCHANGER UNIT, KING PV, 2 | PM | 16.5 | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | WA32385 | HEAT EXCHANGER UNIT, KING PV, 2 | PM | 27.5 | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | WB06687 | HEAT EXCHANGER UNIT, KING PV, 2 | PM |  | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | WB31368 | HEAT EXCHANGER UNIT, KING PV, 2 | PM | 29 | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | WC06864 | HEAT EXCHANGER UNIT, KING PV, 2 | PM | 29.5 | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
HXU2 | E037170 | G | 0749 | FIN TUBE AND FAN COIL UNITS | HEAT EXCHANGER UNIT | TACO | E6206-S | N/A | HEAT EXCH | 2010-07-14 | 2009-07-14 | WC32619 | HEAT EXCHANGER UNIT, KING PV, 2 | PM | 29.5 | 1. INSPECT UNIT FOR LEAKAGE, NON-OPERATING VALVES.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | W850119 | MAKE-UP AIR FAN, KING PV, 2 | PM | 25.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | W875583 | MAKE-UP AIR FAN, KING PV, 2 | PM | 26.75 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | W903536 | MAKE-UP AIR FAN, KING PV, 2 | PM | 26.75 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | W931182 | MAKE-UP AIR FAN, KING PV, 2 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | W959093 | MAKE-UP AIR FAN, KING PV, 2 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | WA06925 | MAKE-UP AIR FAN, KING PV, 2 | PM | 27.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | WA32367 | MAKE-UP AIR FAN, KING PV, 2 | PM | 27.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | WB06666 | MAKE-UP AIR FAN, KING PV, 2 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | WB31351 | MAKE-UP AIR FAN, KING PV, 2 | PM | 34.8 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | WC06861 | MAKE-UP AIR FAN, KING PV, 2 | PM | 29.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
MAF6 | E037165 | G | 0749 | MECHANICAL ROOM 0749 | MAKE-UP AIR FAN | GREENHECK | BSQ-120-4 | 116308940901 | FANS | 2010-07-14 | 2009-07-14 | WC32604 | MAKE-UP AIR FAN, KING PV, 2 | PM | 29.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
NAE38 | E037242 | G | 0749 |  | NETWORK AUTOMATION ENGINE | JOHNSON CO | MS-NAE5510-1 | N/A | DDC | 2010-07-14 | 2009-07-14 | WC08387 | NAE BATTERY REPLACEMENT, 5 YEAR | PM | 71.2 | 1. REPLACE DATA PROTECTION BATTERY. JOHNSON CONTROLS PART NUMBER: MS-BAT1010-0. INTERSTATE BATTERY PART NUMBER: SLA1005. FPM STORES NUMBER: 6177.3743
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | W850120 | ROOM EXHAUST FAN, KING PV, 2 | PM | 25.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | W875584 | ROOM EXHAUST FAN, KING PV, 2 | PM | 26.75 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | W903537 | ROOM EXHAUST FAN, KING PV, 2 | PM | 26.75 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | W931183 | ROOM EXHAUST FAN, KING PV, 2 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | W959094 | ROOM EXHAUST FAN, KING PV, 2 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | WA06926 | ROOM EXHAUST FAN, KING PV, 2 | PM | 27.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | WA32368 | ROOM EXHAUST FAN, KING PV, 2 | PM | 27.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | WB06667 | ROOM EXHAUST FAN, KING PV, 2 | PM |  | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | WB31352 | ROOM EXHAUST FAN, KING PV, 2 | PM | 29 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | WC06862 | ROOM EXHAUST FAN, KING PV, 2 | PM | 29.5 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
REF24 | E037166 | G | 0749 | MECHANICAL ROOM 0749 | ROOM EXHAUST FAN | GREENHECK | BSQ-120-4 | 116308950901 | FANS | 2010-07-14 | 2009-07-14 | WC32605 | ROOM EXHAUST FAN, KING PV, 2 | PM | 35.4 | 1. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 2. INSPECT BELTS & PULLEYS FOR ALIGNMENT, TENSION, AND WEAR. 3. LUBRICATE FAN BEARINGS.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W831747 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM |  | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W845064 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 10.2 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W845649 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 1 | PM | 25.5 | 1. CHECK FITTINGS AND PIPES FOR LEAKS. 2. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 3. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 4. CHECK COUPLING FOR WEAR AND TIGHTEN
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W857334 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 10.2 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W870497 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM |  | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W885145 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM |  | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W898179 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 1 | PM |  | 1. CHECK FITTINGS AND PIPES FOR LEAKS. 2. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 3. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 4. CHECK COUPLING FOR WEAR AND TIGHTEN
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W911931 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM |  | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W925798 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 10.7 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W939794 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 16.35 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W953136 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 1 | PM |  | 1. CHECK FITTINGS AND PIPES FOR LEAKS. 2. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 3. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 4. CHECK COUPLING FOR WEAR AND TIGHTEN
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W967997 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 10.9 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | W978440 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 10.9 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WA06853 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 16.5 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WA20171 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 1 | PM | 22 | 1. CHECK FITTINGS AND PIPES FOR LEAKS. 2. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 3. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 4. CHECK COUPLING FOR WEAR AND TIGHTEN
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WA32308 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 11 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WA45144 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 16.5 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WB06596 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM |  | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WB20227 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 1 | PM |  | 1. CHECK FITTINGS AND PIPES FOR LEAKS. 2. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 3. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 4. CHECK COUPLING FOR WEAR AND TIGHTEN
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WB31296 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 11.6 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WB45318 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 29 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WC06841 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 29.5 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WC20819 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 1 | PM | 23.6 | 1. CHECK FITTINGS AND PIPES FOR LEAKS. 2. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 3. CHECK FOR NOISE AND VIBRATION. IF EXCESSIVE, INITIATE A WORK ORDER TO HAVE THE SHOP INVESTIGATE AND CORRECT THE PROBLEM. 4. CHECK COUPLING FOR WEAR AND TIGHTEN
RTK4 | E037176 | G | 0749 | BUILDING | RECEIVER TANK | BELL & GOS | 102.5CU | QE5942-SA0700855-001 | TANK/CDR | 2010-07-14 | 2009-07-14 | WC32535 | CONDENSATE PUMP/RECEIVER TANK, KING PV, 4 | PM | 29.5 | 1. OPEN TANK DRAIN TO DISCHARGE ANY SEDIMENT. 2. CHECK PUMP FOR PROPER OPERATION BY RAISING THE FLOAT CONTROL OR SWITCHING THE STARTER CONTROL SWITCH TO THE MANUAL POSITION FOR 10 - 30 SECONDS NOTING HOW THE PUMP OPERATES.
SFA1 | E037168 | G | 0749 | ERV-1 | SUPPLY FAN | COMEFRI | P3604002A | 2009/5 | FANS | 2010-07-14 | 2009-07-14
STAIR | E023932 |  |  |  | BUFFER, | MOTORSCRUB |  |  | SHOP EQ. |  | 2010-02-15 | WA10741 | MAINTENACE & REPAIR OF BUFFER, STAIR | EQ-MAINT
TAB1 | E037140 | G | 0734 | STUDIO 1, ROOM 0734 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | N/A | TAB | 2010-07-14 | 2009-07-14 | W831826 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 10.9 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB10 | E037149 | 1 | 1742 | STUDIO 10, ROOM 1742 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118524 | TAB | 2010-07-14 | 2009-07-14 | W857410 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 10.9 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB11 | E037150 | 1 | 1744 | STUDIO 11, ROOM 1744 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118525 | TAB | 2010-07-14 | 2009-07-14 | W885255 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 16.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB12 | E037151 | 1 | 1748 | STUDIO 12, ROOM 1748 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118526 | TAB | 2010-07-14 | 2009-07-14 | W912064 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 22 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB13 | E037152 | 1 | 1752 | STUDIO 13, ROOM 1752 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118527 | TAB | 2010-07-14 | 2009-07-14 | W939901 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 11 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB14 | E037153 | 1 | 1756 | STUDIO 14, ROOM 1756 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118537 | TAB | 2010-07-14 | 2009-07-14 | W968095 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 16.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB15 | E037154 | 1 | 1733 | STUDIO 15, ROOM 1733 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118523 | TAB | 2010-07-14 | 2009-07-14 | WA06951 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 10.9 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB2 | E037141 | G | 0738 | STUDIO 2, ROOM 0738 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | N/A | TAB | 2010-07-14 | 2009-07-14 | WA32385 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 10.9 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB3 | E037142 | G | 0742 | STUDIO 3, ROOM 0742 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118514 | TAB | 2010-07-14 | 2009-07-14 | WB06687 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 16.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB4 | E037143 | G | 0744 | STUDIO 4, ROOM 0744 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118519 | TAB | 2010-07-14 | 2009-07-14 | WB31368 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 22 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB5 | E037144 | G | 0748 | STUDIO 5, ROOM 0748 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118518 | TAB | 2010-07-14 | 2009-07-14 | WC06864 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 11 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB6 | E037145 | G | 0752 | STUDIO 6, ROOM 0752 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118517 | TAB | 2010-07-14 | 2009-07-14 | WC32619 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 16.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB7 | E037146 | G | 0756 | STUDIO 7, ROOM 0756 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118522 | TAB | 2010-07-14 | 2009-07-14 | W850119 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 10.9 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB8 | E037147 | 1 | 1734 | STUDIO 8, ROOM 1734 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118521 | TAB | 2010-07-14 | 2009-07-14 | W875583 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 10.9 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TAB9 | E037148 | 1 | 1738 | STUDIO 9, ROOM 1738 | TERMINAL AIR BOX | ENVIRO TEC | CFR SIZE 1018 | 012209118520 | TAB | 2010-07-14 | 2009-07-14 | W903536 | NIGHT CALL - ERU1 OFF IN ALARM LOW LIMIT -CRAIG WIRTH | HVAC | 16.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TRP1 | E037187 | G | 0749 | ERV1 PREHEAT COIL | TRAP | ARMSTRONG | A5 | N/A | TRAP | 2010-07-14 | 2009-07-14 | W931182 |  |  | 22 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TRP2 | E037188 | G | 0749 | END OF MAIN | TRAP | MEPCO | 44-215A | N/A | TRAP | 2010-07-14 | 2009-07-14 | W959093 |  |  | 11 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TRP3 | E037192 | G | 0749 | END OF MAIN | TRAP | MEPCO | 44-215A | N/A | TRAP | 2010-07-14 | 2009-07-14 |  |  |  | 16.5 | ENERGY RECOVERY VENTILATOR: 1. INSPECT AIR FILTERS (OR MANOMETER DIFFERENTIAL, OR WATER COLUMN). REPLACE FILTER AS NEEDED. CHECK/CLEAN BUILDING AIR INTAKE SCREEN. 2. INSPECT ENERGY WHEEL LABYRINTH SEALS, ADJUST IF NOT SEALING PROPERLY. 3. CHECK TO SE
TRP4 | E037193 | G | 0749 | END OF MAIN | TRAP | MEPCO | 44-215A | N/A | TRAP | 2010-07-14 | 2009-07-14
TRP5 | E037194 | G | 0749 | HXU2 | TRAP | ARMSTRONG | 883T | N/A | TRAP | 2010-07-14 | 2009-07-14
VFD1 | E037184 | G | 0749 | SUPPLY FAN SFA1 | VARIABLE FREQUENCY DRIVE | SQUARE D | A07P09 CLASS 8839 | 46243322000450916 | VFD | 2010-07-14 | 2009-07-14
VFD2 | E037185 | G | 0749 | BUILDING EXHAUST FAN BEF1 | VARIABLE FREQUENCY DRIVE | SQUARE D | A07P09 CLASS 8839 | 46243322000150840 | VFD | 2010-07-14 | 2009-07-14